## HVAC Replacement
Replacement of Low Efficiency HVAC Units
(Converting from Electric Cooling and Heating to Electric Cooling and Gas Heating)
Description of UCRM: |  |  | (Data needed: use of space, age of units)
Data needed for calculations |  |  |  | Description |  |  |  | Resource
A) |  | Tons |  | Cooling Tonnage to be Replaced
B) |  | kW |  | Resistance Heating to be Replaced
C) |  | hrs/yr |  | Cooling Equivalent Full Load Operating Hours (Table 15) |  |  |  | Table 15
D) |  | hrs/yr |  | Heating Equivalent Full Load Operating Hours (Table 16) |  |  |  | Table 16
E) |  | mo/yr |  | Number of Cooling Months
F) |  | mo/yr |  | Number of Heating Months
G) |  | kW/Ton |  | Performance of Existing Cooling Unit (Table 1) |  |  |  | Table 1
H) |  | kW/Ton |  | Performance of New Cooling Unit (Table 1) |  |  |  | Table 1
I) |  | % |  | Efficiency of Proposed Heating Unit (Table 3) |  |  |  | Table 3
J) |  | $/kWh |  | Electrical Energy Rate - Summer
K) |  | $/kWh |  | Electrical Energy Rate - Winter
L) |  | $/Mcf |  | Natural Gas Rate
M) |  | $/kW-mo |  | Electrical Demand Rate - Summer
N) |  | $/kW-mo |  | Electrical Demand Rate - Winter
O) |  |  |  | Enter Diversity of Winter Demand
P) |  | $ |  | Cost of Proposed Unit(s)
Calculations
Q) | Cooling Demand Reduction |  |  | = | A * (G - H) | = | 0 | kW
R) | Annual Cooling Energy Savings |  |  | = | Q * C | = | 0 | kWh/yr
S) | Cooling Demand Savings |  |  | = | Q * E | = | 0 | kW-mo/yr
T) | Cooling Cost Savings |  |  | = | R * J + S * M | = | 0 | $/yr
U) | Original Heating Energy Use |  |  | = | B * D | = | 0 | kWh/yr
V) | Original Heating Energy Cost |  |  | = | U * K + B * F * N * O | = | 0 | $/yr
W) | New Heating Energy Use |  |  | = | U * 3,413 Btuh/kW / I | = | #DIV/0! | Mcf/yr
1,030,000 Btu/Mcf
X) | New Heating Energy Cost |  |  | = | W * L | = | #DIV/0! | $/yr
Y) | Annual Energy Savings |  |  | = | T + V - X | = | #DIV/0! | $/yr
Z) | Simple Payback |  |  | = | P | = | #DIV/0! | yrs
Y