## HVAC Replacement
Replacement of Low Efficiency HVAC Units |  |  |  |  | Calculations
(Converting from Electric Cooling and Heating to Gas Cooling and Heating) |  |  |  |  | R) | Cooling Electrical Demand | = | A * G | = | 0 | kW
Description of UCRM: |  | (Data needed: use of space, age of units) |  |  | S) | Annual Cooling Energy Consumption | = | R * C | = | 0 | kWh/yr
[5 empty] | T) | Cooling Demand Savings | = | R * E | = | 0 | kW-mo/yr
[5 empty] | U) | Equivalent Natural Gas Use for Cooling | = | A * C * 12,000 Btuh/Ton | = | #DIV/0! | Mcf/yr
Data needed for calculations |  |  | Description | Resource |  |  |  | H * 1,030,000 Btu/Mcf
A) | Tons |  | Cooling Tonnage to be Replaced |  | V) | Annual Cost for Gas Cooling | = | U * L | = | #DIV/0! | $/yr
B) | kW |  | Resistance Heating to be Replaced
C) | hrs/yr |  | Cooling Equivalent Full Load Operating Hours | Table 15 | W) | Annual Cost for Electrical Cooling | = | S * J + T * M * N | = | 0 | $/yr
D) | hrs/yr |  | Heating Equivalent Full Load Operating Hours | Table 16
E) | mo/yr |  | Number of Cooling Months |  | X) | Original Annual Heating Energy Use | = | B * D | = | 0 | kWh/yr
F) | mo/yr |  | Number of Heating Months
G) | kW/Ton |  | Performance of Existing Cooling Unit | Table 1 | Y) | Original Annual Heating Energy Cost | = | X * K + B * F * O * P | = | 0 | $/yr
H) | COP |  | Performance of New Cooling Unit
I) | % |  | Efficiency of Proposed Heating Unit |  | Z) | New Annual Heating Energy Use | = | X * 3,413 Btuh/kW / I | = | #DIV/0! | Mcf/yr
J) | $/kWh |  | Electrical Energy Rate - Summer |  |  |  |  | 1,030,000 Btu/Mcf
K) | $/kWh |  | Electrical Energy Rate - Winter |  | AA | New Annual Heating Energy Cost | = | Z * L | = | #DIV/0! | $/yr
L) | $/Mcf |  | Natural Gas Rate
M) | $/kW-mo |  | Electrical Demand Rate - Summer |  | BB) | Annual Energy Savings | = | W - V + Y - AA | = | #DIV/0! | $/yr
N) |  |  | Demand Diversity - Summer Cool (0.0 to 1.0, Default 0.8)
O) | $/kW-mo |  | Electrical Demand Rate - Winter |  | CC) | Simple Payback | = | Q | = | #DIV/0! | yrs
P) |  |  | Enter Diversity of Winter Demand |  |  |  |  | BB
Q) | $ |  | Cost of Proposed Unit(s)