## Temp Control
Temperature Control
(Electric Cooling and Electric or Gas Heating)
Description of UCRM:
Data needed for calculations |  |  | Description |  |  |  | Resource
A) |  | Btu/hr-ft2-°F | U-Value of Walls |  |  |  | Table 18
B) |  | ft2 | Wall Area (includes windows and doors)
C) |  | Btu/hr-ft2-°F | U-Value of Roof |  |  |  | Table 18
D) |  | ft2 | Roof Area
E) |  | °F | Heating Season Thermostat Setpoint
F) |  | °F | Heating Season Thermostat Setback
G) |  | hrs/yr | Heating Season Hours |  |  |  | Table 16
H) |  | °F | Cooling Season Thermostat Setpoint
I) |  | °F | Cooling Season Thermostat Setback
J) |  | hrs/yr | Cooling Season Hours |  |  |  | Table 15
K) |  | % | Heating Equipment Efficiency |  |  |  | Table 3
L) |  | $/Mcf (or kWh) | Natural Gas Rate (or $/winter kWh for electric heat)
M) |  | Btuh/Watt | Performance of Cooling System |  |  |  | Table 1
N) |  | $/kWh | Electrical Energy Rate - Summer
O) |  | $/kWh | Electrical Energy Rate - Winter
P) |  | $ | Implimentation Cost
Calculations
Q) | Total Envelope UA-Value |  | = | A * B + C * D | = | 0 | Btu/hr-°F
R) | Heating Energy Savings |  | = | Q * (E - F) * G | = | 0 | Btu/yr
SG) | Gas Heating Cost Reduction1 |  | = | R * L | = |  | $/yr
(K * 1,030,000 Btu/Mcf)
T) | Cooling Energy Savings |  | = | Q * (H - I) * J | = | 0 | Btu/yr
U) | Cooling Cost Reduction |  | = | T * (N + O) / 2 | = | #DIV/0! | $/yr
1,000 * M
V) | Annual Cost Savings |  | = | S + U | = | #DIV/0! | $/yr
W) | Simple Payback |  | = | P / V | = | #DIV/0! | yrs
1Use SG for Gas Heating and SE for Electrical Heating
SE) | Electrical Heating Cost Reduction |  | = | R * L | = | #DIV/0! | $/yr
3,413 Btuh/kW * K