## Inflitration Reduction
Ventilation Control
(Electric Cooling and Gas Heating)
Description of UCRM: |  |  | (Data needed: use of space, schedule, inside temperature during cooling season,
inside temperature during heating season)
Data needed for calculations |  |  |  | Description |  |  |  | Resource
A) |  | cfm |  | Existing Ventilation Rate
B) |  | cfm |  | Proposed Ventilation Rate
C) |  | °F |  | Avg Inside Temp (DB/WB°F, Cooling Season) |  |  |  | Table 5
D) |  | °F |  | Avg Outside Temp (DB/WB°F, Cooling Season) |  |  |  | Table 5
E) |  | °F |  | Avg Inside Temperature (Heating Season) |  |  |  | Table 5
F) |  | °F |  | Avg Outside Temperature (Heating Season) |  |  |  | Table 5
G) |  | hrs/yr |  | Annual Cooling System Operating Hours |  |  |  | Table 15
H) |  | hrs/yr |  | Annual Heating System Operating Hours |  |  |  | Table 16
I) |  | kW/Ton |  | Performance of Cooling System |  |  |  | Table 1
J) |  | % |  | Efficiency of Heating System |  |  |  | Table 3
K) |  | $/kWh |  | Electrical Energy Rate - Summer
L) |  | $/kWh |  | Electrical Energy Rate - Winter
M) |  | $/kW-mo |  | Electrical Demand Rate - Summer
N) |  | $/kW-mo |  | Electrical Demand Rate - Winter
O) |  | $/Mcf |  | Natural Gas Rate
P) |  | mo/yr |  | Number of Cooling Months (for demand)
Q) |  | $ |  | Cost of Project, Including Design
R) |  | Btu/lbm |  | Enthalpy Inside (From Psychrometric Chart Using C) |  |  |  | P. Chart
S) |  | Btu/lbm |  | Enthalpy Outside (From Psychrometric Chart Using D) |  |  |  | P. Chart
Calculations
T) | Adjusted Ventilation Rate |  |  | = | A - B | = | 0 | cfm
U) | Cooling Energy Savings |  |  | = | 4.5 * T * (R - S) * G | = | 0 | Ton-hrs/yr
12,000 Btu/Ton-hr
V) | Annual Cooling Electrical Energy Savings |  |  | = | U * I | = | 0 | kWh/yr
W) | Cooling Electrical Demand Savings |  |  | = | V | = | #DIV/0! | kW
G
X) | Annual Cooling Cost Savings |  |  | = | V * (K + L)/2 + W * (M + N)/2 * P | = | #DIV/0! | $/yr
Y) | Heating Energy Savings |  |  | = | 1.085 * T * (E - F) * H | = | 0 | Btu/yr
Z) | Annual Natural Gas Savings |  |  | = | Y / J | = | #DIV/0! | Mcf/yr
1,030,000 Btu/Mcf
AA) | Annual Heating Cost Savings |  |  | = | Z * O | = | #DIV/0! | $/yr
BB) | Annual Cost Savings |  |  | = | X + AA | = | #DIV/0! | $/yr
CC) | Simple Payback |  |  | = | Q | = | #DIV/0! | yrs
BB